## Observations
Vision HAZOP excerpt — System 63
Model reading: The drawing depicts the instrument air distribution network and the HHP Air Compressor/Drier Package (63-KC051). It illustrates the supply of instrument air from a main distribution header to various consumers including compressors, gas turbines, and other utility systems, along with the seawater cooling interfaces for the HHP compressor.
# | Deviation | Observation | Tags (status in next sheet)
1 | No flow | The entire instrument air distribution network relies on a single main supply line from W-H063-P-*-U-001. A failure in this main header represents a single point of failure that could lead to a complete loss of instrument air to all connected consumers. | W-H063-P-*-U-001, 2"-AI-634632-AS200-0
2 | No flow, More flow | Note 1 indicates that instrument air take-offs, such as those to 63-JX051 and 63-JX060, are "1" complete with ball valve." Relying on a single manual isolation valve for each connection may not provide sufficient integrity against leakage or accidental closure for critical instrument air users. | 63-4474AI, 63-JX051, 63-4489AI, 63-JX060, NOTE 1
3 | High pressure, Low pressure | The 63-KC051 package has specified operating parameters, including a pressure range of 9.0-10.0 barg. Deviations from these parameters (e.g., high or low pressure) could lead to process upset, equipment damage, or impaired performance of dependent systems. | 63-KC051, HHP AIR COMPRESSOR/DRIER PACKAGE
4 | Low temperature, Blockage | The water trap on the 2"-DO-564731-AS200-0 line requires heat tracing and insulation to maintain 5°C as per Note 2. A failure of this heating system or insulation could lead to freezing of collected water, resulting in a blocked drain and potential line rupture or operational issues. | 2"-DO-564731-AS200-0, NOTE 2
5 | No flow, Less flow, High temperature | The 63-KC051 HHP Air Compressor/Drier Package relies on HO27-P-*-E-003 for seawater supply and return. Loss or reduction of seawater flow, or an increase in its temperature, could cause overheating of the compressor/drier, leading to its shutdown or damage. | HO27-P-*-E-003, 2"-WS-504725-AS200-0, 2"-WS-504726-AS200-0, 63-KC051
6 | Reverse flow, More flow | Instrument air is routed to TO HAZARDOUS OPEN DRAIN (W-H042-P-*-F-003) via line 2"-DO-564732-AS200-0. This connection poses a risk of reverse flow from the drain system into the instrument air system or uncontrolled release of instrument air if not adequately protected or isolated. | W-H042-P-*-F-003, 2"-DO-564732-AS200-0
Vision-generated proposals verified against the tag register - for HAZOP team review, not an authority.

## Tag verification
Tag | Status | Context
W-H063-P-*-U-001 | ukjent format / mulig hallusinasjon | observation 1: No flow
2"-AI-634632-AS200-0 | ukjent format / mulig hallusinasjon | observation 1: No flow
63-4474AI | bekreftet i uttrekket | observation 2: No flow, More flow
63-JX051 | bekreftet i uttrekket | observation 2: No flow, More flow
63-4489AI | NY KANDIDAT - sjekk tegning | observation 2: No flow, More flow
63-JX060 | NY KANDIDAT - sjekk tegning | observation 2: No flow, More flow
NOTE 1 | ukjent format / mulig hallusinasjon | observation 2: No flow, More flow
63-KC051 | bekreftet i uttrekket | observation 3: High pressure, Low pressure
HHP AIR COMPRESSOR/DRIER PACKAGE | ukjent format / mulig hallusinasjon | observation 3: High pressure, Low pressure
2"-DO-564731-AS200-0 | ukjent format / mulig hallusinasjon | observation 4: Low temperature, Blockage
NOTE 2 | ukjent format / mulig hallusinasjon | observation 4: Low temperature, Blockage
HO27-P-*-E-003 | ukjent format / mulig hallusinasjon | observation 5: No flow, Less flow, High temperature
2"-WS-504725-AS200-0 | ukjent format / mulig hallusinasjon | observation 5: No flow, Less flow, High temperature
2"-WS-504726-AS200-0 | ukjent format / mulig hallusinasjon | observation 5: No flow, Less flow, High temperature
63-KC051 | bekreftet i uttrekket | observation 5: No flow, Less flow, High temperature
W-H042-P-*-F-003 | ukjent format / mulig hallusinasjon | observation 6: Reverse flow, More flow
2"-DO-564732-AS200-0 | ukjent format / mulig hallusinasjon | observation 6: Reverse flow, More flow
63-JX051 | bekreftet i uttrekket | symbol-only candidate: manual valve
63-JX060 | NY KANDIDAT - sjekk tegning | symbol-only candidate: manual valve
63-JX061 | NY KANDIDAT - sjekk tegning | symbol-only candidate: manual valve
63-JX053 | bekreftet i uttrekket | symbol-only candidate: manual valve
63-JX054 | NY KANDIDAT - sjekk tegning | symbol-only candidate: manual valve
63-JX057 | bekreftet i uttrekket | symbol-only candidate: manual valve
50-4594WS | NY KANDIDAT - sjekk tegning | symbol-only candidate: manual valve
50-4596WS | bekreftet i uttrekket | symbol-only candidate: manual valve
50-4595WS | bekreftet i uttrekket | symbol-only candidate: manual valve
Totals: 9 verified · 0 verified (normalised) · 6 new candidates · 11 unknown format