## Summary
HAZOP preparation — System 13 (functional loops)
Node | Members | Rows | Rows w/ safeguard | proposed | reviewed | rejected
loop 13-2014 | 13-PDI2014, 13-PI2014 | 2 | 0 | 1 | 1 | 0
loop 13-2254 | 13-PI2254A, 13-PI2254B, 13-PT2254 | 2 | 0 | 2 | 0 | 0
loop 13-2255 | 13-PI2255A, 13-PI2255B, 13-PT2255 | 2 | 0 | 2 | 0 | 0
loop 13-2256 | 13-PI2256A, 13-PI2256B, 13-PT2256 | 2 | 0 | 2 | 0 | 0
loop 13-2260 | 13-PDI2260, 13-PI2260A, 13-PI2260B, 13-PT2260 | 2 | 0 | 2 | 0 | 0
loop 13-2262 | 13-PI2262A, 13-PI2262B, 13-PT2262 | 2 | 0 | 2 | 0 | 0
loop 13-2263 | 13-TI2263, 13-TT2263 | 2 | 0 | 2 | 0 | 0
loop 13-2265 | 13-PI2265, 13-PT2265 | 2 | 0 | 2 | 0 | 0
loop 13-2271 | 13-XV2271, 13-ZL2271, 13-ZS2271 | 4 | 4 | 4 | 0 | 0
loop 13-2272 | 13-XV2272, 13-ZL2272, 13-ZS2272 | 4 | 4 | 4 | 0 | 0
loop 13-2275 | 13-FI2275A, 13-FI2275B, 13-FI2275C | 4 | 0 | 4 | 0 | 0
loop 13-2277 | 13-PI2277, 13-PT2277 | 2 | 0 | 2 | 0 | 0
loop 13-2279 | 13-HS2279, 13-XV2279, 13-XY2279, 13-ZL2279, 13-ZS2279 | 4 | 4 | 4 | 0 | 0
loop 13-2280 | 13-TI2280, 13-TT2280 | 2 | 0 | 2 | 0 | 0
loop 13-2286 | 13-PI2286, 13-TI2286 | 4 | 0 | 4 | 0 | 0
loop 13-2287 | 13-HS2287, 13-ZL2287, 13-ZS2287 | 4 | 0 | 4 | 0 | 0
AI-prepared draft from extracted P&ID/SCD data — for HAZOP team review, not a completed study.

## loop 13-2014
Node: loop 13-2014
Members: 13-PDI2014, 13-PI2014
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | reviewed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2254
Node: loop 13-2254
Members: 13-PI2254A, 13-PI2254B, 13-PT2254
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2255
Node: loop 13-2255
Members: 13-PI2255A, 13-PI2255B, 13-PT2255
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2256
Node: loop 13-2256
Members: 13-PI2256A, 13-PI2256B, 13-PT2256
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2260
Node: loop 13-2260
Members: 13-PDI2260, 13-PI2260A, 13-PI2260B, 13-PT2260
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2262
Node: loop 13-2262
Members: 13-PI2262A, 13-PI2262B, 13-PT2262
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2263
Node: loop 13-2263
Members: 13-TI2263, 13-TT2263
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High temperature | loss of cooling (generic) | possible material/design-limit exceedance (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low temperature | JT-cooling on depressurisation (generic); loss of heating (generic) | possible hydrate formation / brittle fracture risk (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2265
Node: loop 13-2265
Members: 13-PI2265, 13-PT2265
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2271
Node: loop 13-2271
Members: 13-XV2271, 13-ZL2271, 13-ZS2271
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
No flow | blocked line / closed valve (generic); pump/compressor stop (generic) | loss of process function (generic); functions affected: 13-XV2271; safety functions in node: 13-XV2271, 13-ZL2271, 13-ZS2271 | 13-XV2271 | [5 empty] | proposed
Low flow | partial blockage / fouling (generic) | reduced capacity (generic); functions affected: 13-XV2271; safety functions in node: 13-XV2271, 13-ZL2271, 13-ZS2271 | 13-XV2271 | [5 empty] | proposed
High flow | control valve fully open (generic) | possible downstream overload (generic); functions affected: 13-XV2271; safety functions in node: 13-XV2271, 13-ZL2271, 13-ZS2271 | 13-XV2271 | [5 empty] | proposed
Reverse flow | check-valve failure / pressure reversal (generic) | possible contamination / backflow to upstream (generic); functions affected: 13-XV2271; safety functions in node: 13-XV2271, 13-ZL2271, 13-ZS2271 | 13-XV2271 | [5 empty] | proposed

## loop 13-2272
Node: loop 13-2272
Members: 13-XV2272, 13-ZL2272, 13-ZS2272
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
No flow | blocked line / closed valve (generic); pump/compressor stop (generic) | loss of process function (generic); functions affected: 13-XV2272; safety functions in node: 13-XV2272, 13-ZL2272, 13-ZS2272 | 13-XV2272 | [5 empty] | proposed
Low flow | partial blockage / fouling (generic) | reduced capacity (generic); functions affected: 13-XV2272; safety functions in node: 13-XV2272, 13-ZL2272, 13-ZS2272 | 13-XV2272 | [5 empty] | proposed
High flow | control valve fully open (generic) | possible downstream overload (generic); functions affected: 13-XV2272; safety functions in node: 13-XV2272, 13-ZL2272, 13-ZS2272 | 13-XV2272 | [5 empty] | proposed
Reverse flow | check-valve failure / pressure reversal (generic) | possible contamination / backflow to upstream (generic); functions affected: 13-XV2272; safety functions in node: 13-XV2272, 13-ZL2272, 13-ZS2272 | 13-XV2272 | [5 empty] | proposed

## loop 13-2275
Node: loop 13-2275
Members: 13-FI2275A, 13-FI2275B, 13-FI2275C
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
No flow | blocked line / closed valve (generic); pump/compressor stop (generic) | loss of process function (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low flow | partial blockage / fouling (generic) | reduced capacity (generic) | (none found in extraction — verify) | [5 empty] | proposed
High flow | control valve fully open (generic) | possible downstream overload (generic) | (none found in extraction — verify) | [5 empty] | proposed
Reverse flow | check-valve failure / pressure reversal (generic) | possible contamination / backflow to upstream (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2277
Node: loop 13-2277
Members: 13-PI2277, 13-PT2277
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2279
Node: loop 13-2279
Members: 13-HS2279, 13-XV2279, 13-XY2279, 13-ZL2279, 13-ZS2279
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
No flow | blocked line / closed valve (generic); pump/compressor stop (generic) | loss of process function (generic); functions affected: 13-HS2279, 13-XV2279, 13-XY2279; safety functions in node: 13-HS2279, 13-XV2279, 13-ZL2279, 13-ZS2279 | 13-XV2279 | [5 empty] | proposed
Low flow | partial blockage / fouling (generic) | reduced capacity (generic); functions affected: 13-HS2279, 13-XV2279, 13-XY2279; safety functions in node: 13-HS2279, 13-XV2279, 13-ZL2279, 13-ZS2279 | 13-XV2279 | [5 empty] | proposed
High flow | control valve fully open (generic) | possible downstream overload (generic); functions affected: 13-HS2279, 13-XV2279, 13-XY2279; safety functions in node: 13-HS2279, 13-XV2279, 13-ZL2279, 13-ZS2279 | 13-XV2279 | [5 empty] | proposed
Reverse flow | check-valve failure / pressure reversal (generic) | possible contamination / backflow to upstream (generic); functions affected: 13-HS2279, 13-XV2279, 13-XY2279; safety functions in node: 13-HS2279, 13-XV2279, 13-ZL2279, 13-ZS2279 | 13-XV2279 | [5 empty] | proposed

## loop 13-2280
Node: loop 13-2280
Members: 13-TI2280, 13-TT2280
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High temperature | loss of cooling (generic) | possible material/design-limit exceedance (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low temperature | JT-cooling on depressurisation (generic); loss of heating (generic) | possible hydrate formation / brittle fracture risk (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2286
Node: loop 13-2286
Members: 13-PI2286, 13-TI2286
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
High pressure | blocked outlet (generic); upstream pressure source (generic) | possible overpressure of section (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low pressure | upstream supply loss (generic); leak / rupture (generic) | loss of process function / possible gas breakthrough (generic) | (none found in extraction — verify) | [5 empty] | proposed
High temperature | loss of cooling (generic) | possible material/design-limit exceedance (generic) | (none found in extraction — verify) | [5 empty] | proposed
Low temperature | JT-cooling on depressurisation (generic); loss of heating (generic) | possible hydrate formation / brittle fracture risk (generic) | (none found in extraction — verify) | [5 empty] | proposed

## loop 13-2287
Node: loop 13-2287
Members: 13-HS2287, 13-ZL2287, 13-ZS2287
Deviation | Causes | Consequences | Safeguards | S | L | Risk | Recommendation | Action party | Status
No flow | blocked line / closed valve (generic); pump/compressor stop (generic) | loss of process function (generic); functions affected: 13-HS2287; safety functions in node: 13-HS2287, 13-ZL2287, 13-ZS2287 | (none found in extraction — verify) | [5 empty] | proposed
Low flow | partial blockage / fouling (generic) | reduced capacity (generic); functions affected: 13-HS2287; safety functions in node: 13-HS2287, 13-ZL2287, 13-ZS2287 | (none found in extraction — verify) | [5 empty] | proposed
High flow | control valve fully open (generic) | possible downstream overload (generic); functions affected: 13-HS2287; safety functions in node: 13-HS2287, 13-ZL2287, 13-ZS2287 | (none found in extraction — verify) | [5 empty] | proposed
Reverse flow | check-valve failure / pressure reversal (generic) | possible contamination / backflow to upstream (generic); functions affected: 13-HS2287; safety functions in node: 13-HS2287, 13-ZL2287, 13-ZS2287 | (none found in extraction — verify) | [5 empty] | proposed